BANGLADESH UNIVERSITY OF ENGINEERING AND TECHNOLOGY

DEPARTMENT OF ELECTRICAL AND ELECTRONIC ENGINEERING

EEE 306: Power System I Laboratory

(January 2026 Term)

FINAL PROJECT REPORT

Section: C-1    |    Group: 03

Fault Analysis and Protection Coordination of
Ashuganj South 450 MW Combined Cycle Power Plant

Course Instructors:

1. Md. Kamrul Hasan, Lecturer, Department of EEE, BUET

2. Md. Mahadi Jaman, Part-Time Lecturer, Department of EEE, BUET

Signature of Instructor:   ___________________________________________________

Academic Honesty Statement:

IMPORTANT: Please carefully read and sign the Academic Honesty Statement below. We hereby certify that the work presented in this project report is our own work conducted for the EEE 306 course. All sources, simulation tools, literature references, and manufacturer data sheets used have been duly cited.

| Student ID | Student Name | Project Focus / Role | Signature |
| --- | --- | --- | --- |
| 2206136 | Sasshata Talukder | Power Flow & Protection Coordination | ________________ |
| 2206147 | S. M. Sindid Islam Mahodi | Fault Analysis & Symmetrical Components | ________________ |
| 2206152 | Rajib Khan | Network Modeling & Data Verification | ________________ |
| 2206153 | Iftekhar-E-Islam | Simulink Dynamic Model & Relay Logic | ________________ |
| 2206155 | Abu Mohammed Ibn Julker Nahin | Breaker Duty & Station DC System | ________________ |

# Abstract

This report presents a protection coordination and fault analysis of the Ashuganj South 450 MW Combined Cycle Power Plant in Brahmanbaria, Bangladesh. The studied system includes a 360 MW, 458 MVA Siemens generator, a 515 MVA, 22/230 kV step-up transformer, a 230 kV GIS switchyard, auxiliary transformers, and the connection to the national grid. The study was carried out through power-flow analysis, short-circuit analysis, protection coordination, breaker duty assessment, and dynamic simulation. Four types of faults, namely three-phase, single-line-to-ground, line-to-line, and double-line-to-ground faults, were analyzed at different locations. The results showed that the three-phase fault produces the highest fault current, reaching 126.21 kA at the 22 kV generator terminal and 50.53 kA at the 230 kV busbar. The protection coordination study showed no coordination failures, while the dynamic simulation showed that a 230 kV busbar fault was cleared in approximately 87 ms. The power-flow study also showed that the step-up transformer operates at 105.87% of its ONAN rating but only 72.98% of its ODAF rating. An apparent 109.60% loading of the 25 MVA auxiliary transformer was found to be caused by circulating power between two parallel auxiliary transformers rather than an actual overload. The generator neutral grounding limits the earth-fault current to only 7.272 A, indicating the need for dedicated neutral current measurement and earth-fault protection. Overall, the study evaluates the power flow, fault levels, protection coordination, breaker performance, and important operating conditions of the plant. The results are based on simulation and analysis, so the relay settings presented are study values and not actual commissioned plant settings.

# Table of Contents

Updating Table of Contents...

# List of Figures

Updating List of Figures...